North Carolina Department of Agriculture

and Consumer Services

Emergency Programs Division

COMPANION ANIMAL SHELTERING TRAILER (CAST)

Operations Manual

2025

Table of Contents								Page

Trailer Specifications								3

Fire Extinguisher Location							3

Vehicle Requirements								3

Electric Jack									3

Parking									3

Side Door Steps								4

Fresh Water Tank								4

Fuel Tank									5

Generator									5

Hardwire									6

Breaker panel									6

Lights										6

Water Heater									6

HVAC										7

Wastewater Tank								7

Cleaning inside with the hose							8

Back ramp door								8

Side awning doors								9

Trailer specifications

- Estimated weight: 12,000 lbs.

- 8 ft wide x 24 ft long x 7 ft interior height

- 41 total cages

- 23 upper cages – 12 cat portal dividers

- 18 lower cages – 8 removable dividers (store in built-in containers near the back ramp)

Fire extinguisher location – store in sink for transport; place next to side door during sheltering

Vehicle requirements

- F-250 or above/equivalent

- 2 5/16-inch ball, bumper-pull

- Vehicle will need an electronic brake controller

Electric jack

- The jack can be operated manually as well; there is a metal attachment for this in the battery container on the front of the trailer.

Battery container

Parking

- Area needed for operations – 25 ft wide x 45 ft long x 12 ft high

- Park the CAST on as level, hard, well-drained ground as is possible.

- Consider electrical connection for trailer. Ideally connect to hardwire within 24 hours if possible.

- Level trailer side-to-side, then front to back (level location)

- Once unit is level, wheels need to be chocked (chocks location)

- Once wheels are chocked, place corner stabilizer jacks (corner jacks are NOT to be used to lift the trailer, they are just meant to secure it). (location)

Side door steps

- Trailer must be level to use steps – otherwise they will not lie flush with the threshold and the side door will not close completely

- Rotate yellow handle to left or right and carefully ease steps down to the ground.

Fresh water tank – fill on-site or close to destination

- 30-gallon capacity

- Key needed to open

- Use potable water

- Fill is located on curbside front of trailer

- Fill until it is about to run out the top

Fuel tank – fill on-site or close to destination

- 20-gallon capacity

- Located on the front of the trailer under the spare tire

- Fill opening on street side

- Must be NON-ethanol gasoline ONLY. NO EXCEPTIONS.

Power

- Ideally, the on-board trailer generator should only be used for 24 hours before switching to external power.

- Generator operations

  - Hook up the exhaust venturi, located on the street side front. Exhaust pipe is directly under the door to the generator. Venturi kit is stored under the lower cages (streetside).

  - Generator is started inside the trailer at the generator switch panel under the sink

  - To start – hold switch down to the prime position for 5 seconds, release, push switch up to start position, hold and wait for generator to crank

  - Let generator run for 5 minutes before using trailer electricity (the 12-volt lights inside will work on battery power)

  - To turn generator off, press switch down to the stop position

- Hardwire connection (Shoreline plugged in)

  - Shoreline cable located under the sink, access door on the side

  - 50-amp female plug

  - Turn off generator once plugged in

- Breaker panel located under the sink, inside the side door where the Shoreline cord is

- Lights

  - Light switch is just inside the side door

  - 12-volt lights work without generator/hardwire

- Water heater

  - Turn on left handle of faucet (hot water)

  - Turn water pump switch on (under the generator switch panel)

  - Once water is coming out of the faucet, turn the hot water handle off

  - Turn water heater switch on

  - Leave water pump and water heater on for duration of trailer operations

HVAC – Heating, Ventilation, Air Conditioning

- Two (2) 13.5 BTU AC Units with 5.5 BTU Heat, Roof Mounted

  - Must be using generator or hardwire power

  - Adjust thermostat knob to desired temperature

  - Adjust fan speed

- Two (2) 12-Volt Roof Exhaust Fans

  - Open fans with black turn handle

  - Turn numbered knob to desired fan speed

  - Press black switch for exhaust out or air intake

  - Leave closed if not in use

Wastewater tank

- 35-gallon capacity

- Emptying the wastewater tank

  - Option 1: Run a sewer connection from the trailer to an appropriate sewer system (NOT a storm drain)

    - Trailer sewage drain (black) is located to the right of the side door steps

    - Hose is a trip hazard – place cones or similar around it to make workers aware

  - Option 2: Hook up septic truck to system and drain every 24 hours

  - How often you empty the wastewater tank is highly dependent on the number of animals you are housing and the waste that is generated by cleaning

Cleaning inside the trailer using the hose

- Hose hook up is located on the side of the sink (white “spray port”)

- Entire interior of the trailer can be sprayed out if no animals present

- Clean as much large debris (ex. cat litter) out of the cages as possible manually to reduce the chance of the drains clogging

- Spray towards the drains at the back of the cages – they empty into larger drain pipes

- Larger drain pipes that go to the wastewater tank are located at cages U5/L4, U10/L8, U19/L15

  - Insert hose into drain at U1/L1  cleans drain for U1-4/L1-3  drain to pipe at U5/L4

  - Insert hose into drain at U6/L5  cleans drain for U5-10/L4-8 drain to pipe at U10/L8

Back ramp door

- Do not leave locks on when the trailer is occupied/in-use

- Whenever ramp door is down, place pool noodles on cables for safety

Opening the side awning doors (optional)

- All 4 locks must be unlocked on each door (small silver keys)

- The door will swing up as a one-piece unit

- Alternatively, you can open the lower portion and hook at 90 degrees, then raise the awning

- Once awning doors are in the raised position, locks must be placed on arms for safety (located under the sink)